
	[image: image1.jpg]



	DIVISION OF STATE FIRE MARSHAL BUREAU OF FIRE PREVENTION

BOILER SAFETY PROGRAM
	
	Boiler or Pressure Vessel Data Report

FIRST INSPECTION REPORT

	

	This inspection is intended for your safety and the safety of the citizens of Florida.  Your cooperation is greatly appreciated.

	1
	DATE INSPECTED
03/20/2023
	CERT EXP DATE

03/20/2024
	CERTIFICATE POSTED

No
	OWNER EMAIL:

	JURISDICITONAL NUMBER

025576
	NAT’L BD NO.     
13979

	2
	OWNER   
Tailored Brands inc.
	NATURE OF BUSINESS

Retail
	KIND OF INSPECTION

External
	CERTIFICATE INSPECTION

Yes

	
	OWNER STREET ADDRESS

6100 Stevenson Blvd Bldg B
	OWNER CITY

Fremont
	STATE

CA
	94538

	3
	USER NAME – OBJECT LOCATION  

Men’s Wearhouse
	SPECIFIC LOCATION IN PLANT 
Alterations Room
	OBJECT LOCATION - COUNTY

Hillsbourgh

	
	USER STREET ADDRESS

8009 Citrus Park Dr.
	USER CITY

Tampa
	STATE

FL
	ZIP

33625

	4
	TYPE 

Electric Boiler, Miniaure
	YEAR BUILT 
2017
	MANUFACTURER

Pacific
	YEAR INSTALLED

2021

	5
	USE   
Process
	FUEL (BOILER)
Electric
	METHOD OF FIRING (BOILER)

Automatic
	PRESSURE GAGE TESTED

No

	6
	PRESSURE
	SAFETY-RELIEF VALVES

 SET AT  
100
	EXPLAIN IF PRESSURE CHANGED

Not applicable

	
	THIS INSPECTION

100
	PREV INSPECTION  Not applicable
	
	

	7
	IS CONDITION OF OBJECT SUCH THAT A CERTIFICATE MAY BE ISSUED?

      (If no, explain fully on back of form.  List any code violations)   No
	Hydro Test

No

	8
	SHELL

No.       
	DIAMETER

       in.
	 FORMCHECKBOX 
 OD

 FORMCHECKBOX 
 ID
	OVERALL LENGTH

      FT          IN
	THICKNESS

     
	TOTAL HEATING SURFACE (BOILER) 

      Sq.ft.
	MATERIAL

ASME Spec Nos      

	9
	ALLOWABLE STRESS

     
	BUTT STRAP

Thks       in.
	 FORMCHECKBOX 
 Single

 FORMCHECKBOX 
 Double
	HEADERS – WT BOILERS

Thickness       in.
	TYPE

 FORMCHECKBOX 
 Box  FORMCHECKBOX 
 Sinuous  FORMCHECKBOX 
 Wtr. Wall  FORMCHECKBOX 
 Other

	10
	TYPE OF LONGITUDINAL SEAM

Lap     FORMCHECKBOX 
   Butt     FORMCHECKBOX 
  Welded    FORMCHECKBOX 
  Brazed   FORMCHECKBOX 
 Riveted
	RIVETED 

Diam. Hole        in.
	PITCH

      in. X       in.
	SEAM EFF

      %

	11
	HEAD THICKNESS

       in.
	HEAD TYPE     FORMCHECKBOX 
 Plus  FORMCHECKBOX 
 Fixed  FORMCHECKBOX 
 Moveable

 FORMCHECKBOX 
 Minus  FORMCHECKBOX 
 Flat  FORMCHECKBOX 
 Quick Opening
	RADIUS DISH

      in.
	ELLIP RATIO

     
	BOLTING

No.        Dia.       in.  Material      

	12
	TUBESHEET THICKNESS

      in.
	TUBES

No.        Dia.        in.        Length         ft.         in.       
	PITCH (WT BLRS)

      in. X       in.
	LIGAMENT EFF

       %

	13
	FIRE TUBE BOILERS
	DISTANCE UPPER TUBES TO SHELL

Front       in.  Rear       in.
	STAYED AREA

  Front Head
	Above Tubes       

Below Tubes      
	Rear Head
	Above Tubes       

Below Tubes      

	
	STAYS ABOVE TUBES

Front No.        Rear No.       
	TYPE

Head to Head  FORMCHECKBOX 
  Diagonal  FORMCHECKBOX 
  Welded  FORMCHECKBOX 
  Weldless  FORMCHECKBOX 

	AREA OF STAYS

Front        Rear      

	
	STAYS BELOW TUBES

Front No.        Rear No.      
	TYPE

Head to Head  FORMCHECKBOX 
  Diagonal  FORMCHECKBOX 
  Welded  FORMCHECKBOX 
  Weldless  FORMCHECKBOX 

	AREA OF STAYS

Front        Rear      

	14
	FURNACE TYPE

Adamson (No. Sect.)          FORMCHECKBOX 
 Corrugated     FORMCHECKBOX 
 Plain   FORMCHECKBOX 
 Other
	THICKNESS

      in.
	TOTAL LENGTH

      ft.       in.
	TYPE LONG SEAM

 FORMCHECKBOX 
Welded  FORMCHECKBOX 
 Riveted  FORMCHECKBOX 
 Seamless

	15
	STAYBOLTS-TYPE

 FORMCHECKBOX 
 Threaded   FORMCHECKBOX 
 Welded   FORMCHECKBOX 
 Hollow   FORMCHECKBOX 
 Drilled  (size Hole       in) 
	DIAMETER

      in.
	PITCH   

      in. X       in.
	NET AREA

      sq. in.

	16
	SAFETY RELIEF VALVES

No. 1  Size  1”
	TOTL CAPACITY

423 lb/hr

	OUTLETS

No.  1     Size    1”
	PROPERLY DRAINED

X Yes     FORMCHECKBOX 
 No  (If “No” explain on the back of form)  Yes

	17
	STOP VALVES
	ON STEAM LINE

 FORMCHECKBOX 
 Yes   FORMCHECKBOX 
 No
	OTHER CONNECTIONS

 FORMCHECKBOX 
 Yes   FORMCHECKBOX 
 No
	STEAM LINES PROPERLY DRAINED

 FORMCHECKBOX 
 Yes     FORMCHECKBOX 
 No  (If “No” explain on back of form)

	18
	FEED PIPE

Size       in.
	FEED APPLIANCE

No.      
	TYPE DRIVE

 FORMCHECKBOX 
 Steam   FORMCHECKBOX 
 Motor
	CHECK VALVES
	FEED LINE

 FORMCHECKBOX 
 Yes   FORMCHECKBOX 
 No
	Return Lines

 FORMCHECKBOX 
 Yes   FORMCHECKBOX 
 No

	19
	WATER GAGE GLASS

No.      
	TRI- COCKS

No.      
	BLOW OFF PIPE

      Size        in.        Location
	INSPECTION OPENINGS WITH CODE

 FORMCHECKBOX 
 Yes     FORMCHECKBOX 
 No  (If “No” explain on back of form)

	20
	CAST IRON BOILER

Length       in.  Width       in.  Height       in.
	SECTIONS

No.      
	DOES WELDING OF STEAM, FEED, BLOWOFF & OTHER PIPING COMPLY WITH CODE

 FORMCHECKBOX 
 Yes     FORMCHECKBOX 
 No  (If “No” explain on back of form)

	21
	SHOW ALL CODES STAMPING ON BACK OF FORM  Give details – (use sketch)  for special objects NOT covered above - Double wall vessels, etc…
	DOES ALL MATERIAL OTHER THAN AS INDICATED ABOVE COMPLY WITH CODE

 FORMCHECKBOX 
 Yes     FORMCHECKBOX 
 No  (If “No” explain on back of form)

	22
	NAME AND TITLE OF PERSON WHOM REQUIREMENTS WERE EXPLAINED:



	23
	I HEREBY CERTIFY THIS IS A TRUE REPORT OF MY INSPECTION

Signature of Inspector: 

Luke O’Toole
	IDENT. NO

FL-23-000069

NB-9592

	 EMPLOYED BY

 XL Insurance

	IDENT. NO.
9592LO


	D14-380    10-01-2000


Data Plate Information;
VIOLATIONS:  
21 - 7.1.6 WATER GAGE GLASS LEAKING - gaskets leaking causing buildup around glass
REF: NBIC 2017, PART 2, PARA 2.2.10.4(A5) - ANY LEAKAGE AT THESE FITTINGS (WATER GAGE GLASS) SHOULD BE PROMPTLY CORRECTED TO AVOID DAMAGE TO THE FITTINGS OR A FALSE WATERLINE INDICATION. REF NBIC 2017, PART 1, PARA 2.2.10.6 (J) - IF THE CONTROLS ARE INOPERATIVE OR THE CORRECT WATER LEVEL IS NOT INDICATED, THE BOILER SHALL BE TAKEN OUT OF SERVICE UNTIL THE UNSAFE CONDITION HAS BEEN CORRECTED.

Update March 20, 2023 - Open, no action taken
21 - 8.2.3.1 CONDENSATE TANK WATER LEVEL CONTROL OR FLOAT - Tank corrosion
REF: NBIC PART 1, 2017 2.7.4 CONDENSATE AND RETURN Each condensate return pump, where practicable, shall be provided with an automatic water level control set to maintain an adequate water level in the condensate tank.

Update March 20, 2023 - Open no action taken



         


____M___                                          _______13797__                               _     


     ASME STAMP                                      National Board Number                           Serial Number











                             Pacific                                                                                     2017    _________________________ ______________________             		    ______


                                 Manufactured By                                                     	       Year














____100  PSI____                                  _____423 lb/hr___


       MAWP                                                         CAPACITY









